## CALCULATOR
[7 empty] | Panduit Patch Cord Approximate Diameters | [5 empty] | Cat 6A Plenum UTP Cable | Dia. (in.)
[13 empty] | Panduit Vari-MaTriX HD | 0.23
[7 empty] | Cat. | AWG | in. |  | mm |  | Panduit Std Comp+ HD | 0.23
[7 empty] | 5e | 28 | 0.149 |  | 3.7846 |  | CommScope 2091B | 0.285
[7 empty] | 5e | 24 | 0.215 |  | 5.461 |  | CommScope 2091SD | 0.265
[7 empty] | 6 | 28 | 0.15 |  | 3.81 |  | Belden 10GXS | 0.265
Enter the cable diameter below and select in. or mm. | [6 empty] | 6 | 24 | 0.235 |  | 5.969 |  | Berk-Tek LANmark-XTP | 0.275
[7 empty] | 6A | 28 | 0.185 |  | 4.699
Cable Diameter = | 0.23 | 1 |  |  |  |  | 6A | 24 | 0.25 |  | 6.35
| Duplex Cable? | 1
Product Family | Part Number | Description | Cable Manager Area |  |  | Recommended Cable Fill (30%) |  |  |  | Maximum Cable Fill (50%)
|  |  | Front Usable Area (sq. in.) | Rear Usable Area (sq. in.) | Total Usable Area (sq. in.) | Front | Rear | Total |  | Front | Rear | Total
PR2V PatchRunner™ 2 Vertical Cable Managers | PR2VD06 | 6" wide | 45.11 | 27.26 | 72.37 | 325 | 196 | 522 |  | 542 | 328 | 870
| PR2VFD06 | 6" wide, front only | 45.11 | 0 | 45.11 | 325 | 0 | 325 |  | 542 | 0 | 542
| PR2VD08 | 8" wide | 63.71 | 39.73 | 103.44 | 460 | 286 | 746 |  | 766 | 478 | 1244
| PR2VFD08 | 8" wide, front only | 63.71 | 0 | 63.71 | 460 | 0 | 460 |  | 766 | 0 | 766
| PR2VD10 | 10" wide | 82.31 | 52.21 | 134.52 | 594 | 376 | 971 |  | 990 | 628 | 1618
| PR2VFD10 | 10" wide, front only | 82.31 | 0 | 82.31 | 594 | 0 | 594 |  | 990 | 0 | 990
| PR2VD12 | 12" wide | 100.9 | 64.68 | 165.58 | 728 | 467 | 1195 |  | 1214 | 778 | 1992
| PR2VFD12 | 12" wide, front only | 100.9 | 0 | 100.9 | 728 | 0 | 728 |  | 1214 | 0 | 1214
| Single PR2V Finger |  |  |  | 5.8 | 41 |  |  |  | 69
PR2VRG PatchRunner™2 Rear Gate Accessory | PR2VRGSK06 | 6" wide gate kit | 0 | 43.45 | 43.45 | 0 | 313 | 313 |  | 0 | 522 | 522
| PR2VRGSK08 | 8" wide gate kit | 0 | 59.51 | 59.51 | 0 | 429 | 429 |  | 0 | 716 | 716
| PR2VRGSK10 | 10" wide gate kit | 0 | 75.57 | 75.57 | 0 | 545 | 545 |  | 0 | 909 | 909
| PR2VRGSK12 | 12" wide gate kit | 0 | 91.63 | 91.63 | 0 | 661 | 661 |  | 0 | 1102 | 1102
PR2HF PatchRunner™2 Horizontal Cable Managers | PR2HF2 | 2RU, front only | 12.5639 | 0 | 12.5639 | 90 | 0 | 90 |  | 151 | 0 | 151
| PR2HF3 | 3RU, front only | 23.0956 | 0 | 23.0956 | 166 | 0 | 166 |  | 277 | 0 | 277
| PR2HF4 | 4RU, front only | 33.6272 | 0 | 33.6272 | 242 | 0 | 242 |  | 404 | 0 | 404
PE2V PatchRunner™ 2 High Capacity Vertical Cable Managers | PE2VD06 | 6" wide | 66.1018 | 44.2782 | 110.38 | 477 | 319 | 797 |  | 795 | 532 | 1328
| PE2VFD06 | 6" wide, front only | 66.1018 | 0 | 66.1018 | 477 | 0 | 477 |  | 795 | 0 | 795
| PE2VD08 | 8" wide | 92.4809 | 63.0973 | 155.5782 | 667 | 455 | 1123 |  | 1112 | 759 | 1872
| PE2VFD08 | 8" wide, front only | 92.4809 | 0 | 92.4809 | 667 | 0 | 667 |  | 1112 | 0 | 1112
| PE2VD10 | 10" wide | 118.8599 | 81.9639 | 200.8238 | 858 | 591 | 1450 |  | 1430 | 986 | 2416
| PE2VFD10 | 10" wide, front only | 118.8599 | 0 | 118.8599 | 858 | 0 | 858 |  | 1430 | 0 | 1430
| PE2VD12 | 12" wide | 145.239 | 100.7355 | 245.9745 | 1048 | 727 | 1776 |  | 1747 | 1212 | 2960
| PE2VFD12 | 12" wide, front only | 145.239 | 0 | 145.239 | 1048 | 0 | 1048 |  | 1747 | 0 | 1747
| Single PE2V Finger |  |  |  | 5.8 | 41 |  |  |  | 69
WMPV NetRunner™ Vertical Cable Managers | WMPV22E | 4.9" wide, 22RU | 17.3 | 17.3 | 34.6 | 124 | 124 | 249 |  | 208 | 208 | 416
| WMPVF22E | 4.9" wide, 22RU, front only | 17.3 | 0 | 17.3 | 124 | 0 | 124 |  | 208 | 0 | 208
| WMPV45E | 4.9" wide, 45RU | 17.3 | 17.3 | 34.6 | 124 | 124 | 249 |  | 208 | 208 | 416
| WMPVF45E | 4.9" wide, 45RU, front only | 17.3 | 0 | 17.3 | 124 | 0 | 124 |  | 208 | 0 | 208
| WMPVHC45E | 6.7" wide, 45RU | 30.7 | 30.7 | 61.4 | 221 | 221 | 443 |  | 369 | 369 | 738
| WMPVHCF45E | 6.7" wide, 45RU, front only | 30.7 | 0 | 30.7 | 221 | 0 | 221 |  | 369 | 0 | 369
| Single WMPV Finger |  |  |  | 3.7 | 26 |  |  |  | 44
| Single WMPVHC Finger |  |  |  | 4.7 | 33 |  |  |  | 56
NRV NetRunner™ High Capacity Vertical Cable Managers | NRV10 | 10" wide, 45RU | 49.1 | 49.1 | 98.2 | 354 | 354 | 709 |  | 590 | 590 | 1181
| NRVF10 | 10" wide, 45RU, front only | 49.1 | 0 | 49.1 | 354 | 0 | 354 |  | 590 | 0 | 590
| Single NRV Finger |  |  |  | 4.7 | 33 |  |  |  | 56
WMP PatchLink™ Horizontal Cable Managers | WMP1E | 2RU, front/rear | 7.6 | 10.6 | 18.2 | 54 | 76 | 131 |  | 91 | 127 | 219
| WMPF1E | 2RU, front only | 7.6 | 0 | 7.6 | 54 | 0 | 54 |  | 91 | 0 | 91
| WMPH2E | 2RU, front/rear, w/ bend rad. clips | 5.9 | 10.6 | 16.5 | 42 | 76 | 119 |  | 71 | 127 | 198
| WMPHF2E | 2RU, front only, w/ bend rad. clips | 5.9 | 0 | 5.9 | 42 | 0 | 42 |  | 71 | 0 | 71
| WMPSE | 1RU, front/rear | 3.5 | 6.3 | 9.8 | 25 | 45 | 70 |  | 42 | 75 | 117
| WMPFSE | 1RU, front only | 3.5 | 0 | 3.5 | 25 | 0 | 25 |  | 42 | 0 | 42
| WMPLSE | 1RU, front/rear, short depth | 2.1 | 6.3 | 8.4 | 15 | 45 | 60 |  | 25 | 75 | 101
| WMPLFSE | 1RU, front only, short depth | 2.1 | 0 | 2.1 | 15 | 0 | 15 |  | 25 | 0 | 25
Note: Rear section may be partially blocked by rack posts
NCMH NetManager™ Horizontal Cable Managers | NCMH2 | 2RU, front/rear | 6 | 8 | 14 | 43 | 57 | 101 |  | 72 | 96 | 168
| NCMHF2 | 2RU, front only | 6 | 0 | 6 | 43 | 0 | 43 |  | 72 | 0 | 72
| NCMHF1 | 1RU, front only | 2.3 | 0 | 2.3 | 16 | 0 | 16 |  | 27 | 0 | 27
NM NetManager™ High Capacity Horizontal Cable Managers | NM1 | 1RU, front/rear | 3.3 | 4.1 | 7.4 | 23 | 29 | 53 |  | 39 | 49 | 89
| NMF1 | 1RU, front only | 3.3 | 0 | 3.3 | 23 | 0 | 23 |  | 39 | 0 | 39
| NM2 | 2RU, front/rear | 9.8 | 11.1 | 20.9 | 70 | 80 | 150 |  | 117 | 133 | 251
| NMF2 | 2RU, front only | 9.8 | 0 | 9.8 | 70 | 0 | 70 |  | 117 | 0 | 117
| NM3 | 3RU, front/rear | 17.3 | 22 | 39.3 | 124 | 158 | 283 |  | 208 | 264 | 472
| NMF3 | 3RU, front only | 17.3 | 0 | 17.3 | 124 | 0 | 124 |  | 208 | 0 | 208
| NM4 | 4RU, front/rear | 24.3 | 31.9 | 56.2 | 175 | 230 | 405 |  | 292 | 383 | 676
| NMF4 | 4RU, front only | 24.3 | 0 | 24.3 | 175 | 0 | 175 |  | 292 | 0 | 292
Note: Rear section may be partially blocked by rack posts
CMPH Open-Access™ Horizontal Cable Managers | CMPH1 | 1RU, front/rear | 2.3 | 2.9 | 5.2 | 16 | 20 | 37 |  | 27 | 34 | 62
| CMPHF1 | 1RU, front only | 2.3 | 0 | 2.3 | 16 | 0 | 16 |  | 27 | 0 | 27
| CMPH2 | 2RU, front/rear | 5.3 | 10.8 | 16.1 | 38 | 77 | 116 |  | 63 | 129 | 193
| CMPHF2 | 2RU, front only | 5.3 | 0 | 5.3 | 38 | 0 | 38 |  | 63 | 0 | 63
| CMPHH2 | 2RU, front only, larger D-rings | 10.8 | 0 | 10.8 | 77 | 0 | 77 |  | 129 | 0 | 129
| CMPHHF1 | 1RU, front only, larger D-rings | 2.9 | 0 | 2.9 | 20 | 0 | 20 |  | 34 | 0 | 34
Note: Rear section may be partially blocked by rack posts
PEHF PatchRunner™ High Capacity Horizontal Cable Managers | PEHF2 | 2RU, front only | 16.6 | 0 | 16.6 | 119 | 0 | 119 |  | 199 | 0 | 199
| PEHF3 | 3RU, front only | 29.6 | 0 | 29.6 | 213 | 0 | 213 |  | 356 | 0 | 356
| PEHF4 | 4RU, front only | 42.8 | 0 | 42.8 | 309 | 0 | 309 |  | 515 | 0 | 515
CMVDR Vertical D-rings | CMVDR1 | 5.70"L x 2.00"W |  |  | 6 |  |  | 43 |  |  |  | 72
| CMVDR1S | 3.30"L x 2.00"W |  |  | 3 |  |  | 21 |  |  |  | 36
| CMVDR2 | 5.70"L x 3.00"W |  |  | 10.8 |  |  | 77 |  |  |  | 129
| CMVDR2S | 3.30"L x 3.00"W |  |  | 6 |  |  | 43 |  |  |  | 72
| CMVDRC | between-racks, 5.60"L x 8.00"W |  |  | 24 |  |  | 173 |  |  |  | 288
CM Cable Routing Troughs | CMLT19 | lower trough w/ bend radius |  |  | 22.7 |  |  | 163 |  |  |  | 273
| CMUT19 | upper trough w/ bend radius |  |  | 8.2 |  |  | 59 |  |  |  | 98
| CMT4 | horizontal trough |  |  | 21.9 |  |  | 158 |  |  |  | 263
*Capacity is calculated for within the trough channel only. Higher capacities can be achieved when cables are tied together.
CWMPV IN-Cabinet Vertical Cable Manager | CWMPV2418 | side mount, 2"W x 4"D x 2.6'H | 5.7 | 0 | 5.7 | 41 | 0 | 41 |  | 68 | 0 | 68
| CWMPV3418 | side mount, 3"W x 4"D x 2.6'H | 9.1 | 0 | 9.1 | 65 | 0 | 65 |  | 109 | 0 | 109
| CWMPV2440 | side mount, 2"W x 4"D x 6'H | 5.7 | 0 | 5.7 | 41 | 0 | 41 |  | 68 | 0 | 68
| CWMPV3440 | side mount, 3"W x 4"D x 6'H | 9.1 | 0 | 9.1 | 65 | 0 | 65 |  | 109 | 0 | 109
| CWMPV2318 | side mount, 2"W x 3"D x 2.6'H | 5.2 | 0 | 5.2 | 37 | 0 | 37 |  | 62 | 0 | 62
| CWMPV3318 | side mount, 3"W x 3"D x 2.6'H | 7.8 | 0 | 7.8 | 56 | 0 | 56 |  | 93 | 0 | 93
| CWMPV2340 | side mount, 2"W x 3"D x 6'H | 5.2 | 0 | 5.2 | 37 | 0 | 37 |  | 62 | 0 | 62
| CWMPV3340 | side mount, 3"W x 3"D x 6'H | 7.8 | 0 | 7.8 | 56 | 0 | 56 |  | 93 | 0 | 93
4-Post Rack Vertical Tie-off Panels | V4PTOB | Vertical Tie-off Panel with AR4P 4-Post Racks mount brackets | 31.7 | 0 | 31.7 | 228 | 0 | 228 |  | 381 | 0 | 381
| V4PTOB | Vertical Tie-off Panel with R4P 4-Post Racks mount brackets | 35.8 | 0 | 35.8 | 258 | 0 | 258 |  | 430 | 0 | 430
J-PRO & J-MOD J Hooks | JP75^ | J-Pro™ cable support, 0.75" |  |  | 0.626 |  |  | 6 |  |  |  | 6
| JP131^ | J-Pro™ cable support, 1.31" |  |  | 1.74 |  |  | 16 |  |  |  | 16
| JP2^ | J-Pro™ cable support, 2.0" |  |  | 3.155 |  |  | 30 |  |  |  | 30
| JP4^ | J-Pro™ cable support, 4.0" |  |  | 13.478 |  |  | 129 |  |  |  | 129
| JMJH2^ | J-Mod™ cable support, 2.0" |  |  | 3.037 |  |  | 29 |  |  |  | 29
*Capacity is calculated for J Hooks with a 50% recommended fill and 70% maximum fill.
EMT Electrical Metallic Tubing | 1/2" | Useable Inside Diameter in inches | 0.622 |  | 0.30398 |  |  | 2 |  |  |  | 2
| 3/4" | Useable Inside Diameter in inches | 0.824 |  | 0.53348 |  |  | 5 |  |  |  | 5
| 1" | Useable Inside Diameter in inches | 1.049 |  | 0.8646 |  |  | 8 |  |  |  | 8
| 1-1/4" | Useable Inside Diameter in inches | 1.38 |  | 1.4963 |  |  | 14 |  |  |  | 14
| 1-1/2" | Useable Inside Diameter in inches | 1.61 |  | 2.0366 |  |  | 19 |  |  |  | 19
| 2" | Useable Inside Diameter in inches | 2.067 |  | 3.357 |  |  | 32 |  |  |  | 32
| 2-1/2" | Useable Inside Diameter in inches | 2.731 |  | 5.8601 |  |  | 56 |  |  |  | 56
| 3" | Useable Inside Diameter in inches | 3.356 |  | 8.8493 |  |  | 85 |  |  |  | 85
| 3-1/2" | Useable Inside Diameter in inches | 3.834 |  | 11.5497 |  |  | 111 |  |  |  | 111
| 4" | Useable Inside Diameter in inches | 4.334 |  | 14.7585 |  |  | 142 |  |  |  | 142
*Capacity is calculated for J Hooks with a 50% recommended fill and 70% maximum fill.
EMT Electrical Metallic Tubing* | 1/2" | Useable Inside Diameter in inches | 0.622 |  | 0.30398 |  |  | 2 |  |  |  | 2
| 3/4" | Useable Inside Diameter in inches | 0.824 |  | 0.53348 |  |  | 5 |  |  |  | 5
| 1" | Useable Inside Diameter in inches | 1.049 |  | 0.8646 |  |  | 8 |  |  |  | 8
| 1-1/4" | Useable Inside Diameter in inches | 1.38 |  | 1.4963 |  |  | 14 |  |  |  | 14
| 1-1/2" | Useable Inside Diameter in inches | 1.61 |  | 2.0366 |  |  | 19 |  |  |  | 19
| 2" | Useable Inside Diameter in inches | 2.067 |  | 3.357 |  |  | 32 |  |  |  | 32
| 2-1/2" | Useable Inside Diameter in inches | 2.731 |  | 5.8601 |  |  | 56 |  |  |  | 56
| 3" | Useable Inside Diameter in inches | 3.356 |  | 8.8493 |  |  | 85 |  |  |  | 85
| 3-1/2" | Useable Inside Diameter in inches | 3.834 |  | 11.5497 |  |  | 111 |  |  |  | 111
| 4" | Useable Inside Diameter in inches | 4.334 |  | 14.7585 |  |  | 142 |  |  |  | 142
*Capacity is calculated for conduit at 40% maximum per NEC guidelines
IMC Intermediate Conduit* | 1/2" | Useable Inside Diameter in inches | 0.675 |  | 0.35799 |  |  | 3 |  |  |  | 3
| 3/4" | Useable Inside Diameter in inches | 0.879 |  | 0.60708 |  |  | 5 |  |  |  | 5
| 1" | Useable Inside Diameter in inches | 1.12 |  | 0.9856 |  |  | 9 |  |  |  | 9
| 1-1/4" | Useable Inside Diameter in inches | 1.468 |  | 1.6932 |  |  | 16 |  |  |  | 16
| 1-1/2" | Useable Inside Diameter in inches | 1.703 |  | 2.2787 |  |  | 21 |  |  |  | 21
| 2" | Useable Inside Diameter in inches | 2.17 |  | 3.6999 |  |  | 35 |  |  |  | 35
| 2-1/2" | Useable Inside Diameter in inches | 2.597 |  | 5.2992 |  |  | 51 |  |  |  | 51
| 3" | Useable Inside Diameter in inches | 3.216 |  | 8.1264 |  |  | 78 |  |  |  | 78
| 3-1/2" | Useable Inside Diameter in inches | 3.711 |  | 10.8205 |  |  | 104 |  |  |  | 104
| 4" | Useable Inside Diameter in inches | 4.205 |  | 13.893 |  |  | 133 |  |  |  | 133
*Capacity is calculated for conduit at 40% maximum per NEC guidelines
Rigid Conduit Steel or Aluminum* | 1/2" | Useable Inside Diameter in inches | 0.622 |  | 0.30398 |  |  | 2 |  |  |  | 2
| 3/4" | Useable Inside Diameter in inches | 0.824 |  | 0.53348 |  |  | 5 |  |  |  | 5
| 1" | Useable Inside Diameter in inches | 1.049 |  | 0.8646 |  |  | 8 |  |  |  | 8
| 1-1/4" | Useable Inside Diameter in inches | 1.38 |  | 1.4963 |  |  | 14 |  |  |  | 14
| 1-1/2" | Useable Inside Diameter in inches | 1.61 |  | 2.0366 |  |  | 19 |  |  |  | 19
| 2" | Useable Inside Diameter in inches | 2.067 |  | 3.357 |  |  | 32 |  |  |  | 32
| 2-1/2" | Useable Inside Diameter in inches | 2.469 |  | 4.7897 |  |  | 46 |  |  |  | 46
| 3" | Useable Inside Diameter in inches | 3.068 |  | 7.3956 |  |  | 71 |  |  |  | 71
| 3-1/2" | Useable Inside Diameter in inches | 3.548 |  | 9.8908 |  |  | 95 |  |  |  | 95
| 4" | Useable Inside Diameter in inches | 4.026 |  | 12.7354 |  |  | 122 |  |  |  | 122
| 5" | Useable Inside Diameter in inches | 5.047 |  | 20.0139 |  |  | 192 |  |  |  | 192
| 6" | Useable Inside Diameter in inches | 6.065 |  | 28.9019 |  |  | 278 |  |  |  | 278
*Capacity is calculated for conduit at 40% maximum per NEC guidelines
Cable Capacity Calculator V11

## numbers (hidden)
in. | no
mm | yes
30% | 40%
50% | 40%
0.215 | 0.185 | 0.275 | 0.15 | 0.235